## EPPC OID
upsEIdentity
| upsEIdentityManufacturer.0 | .1.3.6.1.4.1.935.10.1.1.1.1
| upsEIdentityModel.0 | .1.3.6.1.4.1.935.10.1.1.1.2
| upsEIdentityUPSFirmwareVerison.0 | .1.3.6.1.4.1.935.10.1.1.1.3
| upsEIndentityUPSSerialNumber.0 | .1.3.6.1.4.1.935.10.1.1.1.4
| upsEIdentityDescription.0 | .1.3.6.1.4.1.935.10.1.1.1.5
| upsEIdentityAgentSoftwareVerison.0 | .1.3.6.1.4.1.935.10.1.1.1.6
| upsEIdentityAttachedDevices.0 | .1.3.6.1.4.1.935.10.1.1.1.7
upsESystemSummary
| upsESystemStatus.0 | .1.3.6.1.4.1.935.10.1.1.2.1
| upsESystemTemperature.0 | .1.3.6.1.4.1.935.10.1.1.2.2
| upsESystemWarningCode.0 | .1.3.6.1.4.1.935.10.1.1.2.3
| upsESystemFaultCode.0 | .1.3.6.1.4.1.935.10.1.1.2.4
| upsESystemConfigInputVoltage.0 | .1.3.6.1.4.1.935.10.1.1.2.5
| upsESystemConfigInputFrequence.0 | .1.3.6.1.4.1.935.10.1.1.2.6
| upsESystemConfigOutputVoltage.0 | .1.3.6.1.4.1.935.10.1.1.2.7
| upsESystemConfigOutputFrequency.0 | .1.3.6.1.4.1.935.10.1.1.2.8
| upsESystemConfigOutputVA.0 | .1.3.6.1.4.1.935.10.1.1.2.9
| upsESystemConfigOutputPower.0 | .1.3.6.1.4.1.935.10.1.1.2.10
| upsESystemConfigOutputLoadHighSetPoint.0 | .1.3.6.1.4.1.935.10.1.1.2.11
| upsESystemConfigOverTemperatureSetPoint.0 | .1.3.6.1.4.1.935.10.1.1.2.12
| upsESystemInputSourceNum.0 | .1.3.6.1.4.1.935.10.1.1.2.13
| upsESystemInputLineBads.0 | .1.3.6.1.4.1.935.10.1.1.2.14
| upsESystemInputNumPhases.0 | .1.3.6.1.4.1.935.10.1.1.2.16.1.1
ups Esystem Input Table | upsESystemInputFrequency.1 | .1.3.6.1.4.1.935.10.1.1.2.16.1.2
upsESystemInputFrequency.2
upsESystemInputFrequency.3
| upsESystemInputVoltage.1 | .1.3.6.1.4.1.935.10.1.1.2.16.1.3
upsESystemInputVoltage.2
upsESystemInputVoltage.3
| upsESystemInputCurrent.1 | .1.3.6.1.4.1.935.10.1.1.2.16.1.4
upsESystemInputCurrent.2
upsESystemInputCurrent.3
| upsESystemInputWatts.1 | .1.3.6.1.4.1.935.10.1.1.2.16.1.5
upsESystemInputWatts.2
upsESystemInputWatts.3
| upsESystemOutputNumPhase.0 | .1.3.6.1.4.1.935.10.1.1.2.17
ups Esystem Output Table | upsESystemOutputFrequency.1 | .1.3.6.1.4.1.935.10.1.1.2.18.1.2
upsESystemOutputFrequency.2
upsESystemOutputFrequency.3
| upsESystemOutputVoltage.1 | .1.3.6.1.4.1.935.10.1.1.2.18.1.3
upsESystemOutputVoltage.2
upsESystemOutputVoltage.3
| upsESystemOutputCurrent.1 | .1.3.6.1.4.1.935.10.1.1.2.18.1.4
upsESystemOutputCurrent.2
upsESystemOutputCurrent.3
| upsESystemOutputWatts.1 | .1.3.6.1.4.1.935.10.1.1.2.18.1.5
upsESystemOutputWatts.2
upsESystemOutputWatts.3
| upsESystemOutputVA.1 | .1.3.6.1.4.1.935.10.1.1.2.18.1.6
upsESystemOutputVA.2
upsESystemOutputVA.3
| upsESystemOutputLoad.1 | .1.3.6.1.4.1.935.10.1.1.2.18.1.7
upsESystemOutputLoad.2
upsESystemOutputLoad.3
| upsESystemBypassNumPhase.0 | .1.3.6.1.4.1.935.10.1.1.2.19
ups Esystem Bypass Table | upsESystemBypassFrequency.1 | .1.3.6.1.4.1.935.10.1.1.2.20.1.2
upsESystemBypassFrequency.2
upsESystemBypassFrequency.3
| upsESystemBypassVoltage.1 | .1.3.6.1.4.1.935.10.1.1.2.20.1.3
upsESystemBypassVoltage.2
upsESystemBypassVoltage.3
| upsESystemBypassCurrent.1 | .1.3.6.1.4.1.935.10.1.1.2.20.1.4
upsESystemBypassCurrent.2
upsESystemBypassCurrent.3
| upsESystemBypassWatts.1 | .1.3.6.1.4.1.935.10.1.1.2.20.1.5
upsESystemBypassWatts.2
upsESystemBypassWatts.3
| upsESystemConfigBelowCapacityLimit.0 | .1.3.6.1.4.1.935.10.1.1.2.21
| upsESystemConfigBelowRemainTimeLimit.0 | .1.3.6.1.4.1.935.10.1.1.2.22
| upsEShutdownwarningPeriodTime.12 | .1.3.6.1.4.1.935.10.1.1.8.4.1.3
| upsEShutdownWarningPeriodInterval.12 | .1.3.6.1.4.1.935.10.1.1.8.4.1.4
upsEBatterySystem
| upsEBatteryStatus.0 | .1.3.6.1.4.1.935.10.1.1.3.1
| upsESecondsOnBattery.0 | .1.3.6.1.4.1.935.10.1.1.3.2
| upsEBatteryEstimatedMinutesRemaining.0 | .1.3.6.1.4.1.935.10.1.1.3.3
| upsEBatteryEstimatedChargeRemaining.0 | .1.3.6.1.4.1.935.10.1.1.3.4
| upsEPositiveBatteryVoltage.0 | .1.3.6.1.4.1.935.10.1.1.3.5
| upsENegativeBatteryVoltage.0 | .1.3.6.1.4.1.935.10.1.1.3.6
| upsEBatteryCellNumber.0 | .1.3.6.1.4.1.935.10.1.1.3.7
| upsEBatteryTemperature.0 | .1.3.6.1.4.1.935.10.1.1.3.8
| upsEBatteryLastReplacedDate.0 | .1.3.6.1.4.1.935.10.1.1.3.9
| upsEBatteryABMStatus.0 | .1.3.6.1.4.1.935.10.1.1.3.10
UPS EchargeModules Table | upsEChargerModulesNum.0 | .1.3.6.1.4.1.935.10.1.1.3.11
upsEPowerConverterSystem (Gripower)
| upsEUPSModulesNum.0 | .1.3.6.1.4.1.935.10.1.1.4.1
upsEModulesTable | upsEModuleAddress.1….n | .1.3.6.1.4.1.935.10.1.1.4.2.1.2
| upsEModulePositiveBusVolt.1….n | .1.3.6.1.4.1.935.10.1.1.4.2.1.3
| upsEModuleNegativeBusVolt.1….n | .1.3.6.1.4.1.935.10.1.1.4.2.1.4
| upsEModuleTemperature.1….n | .1.3.6.1.4.1.935.10.1.1.4.2.1.5
| upsEModuleWorkingMode.1…n | .1.3.6.1.4.1.935.10.1.1.4.2.1.6
| upsEModuleOutputCurrentR.1…n | .1.3.6.1.4.1.935.10.1.1.4.2.1.7
| upsEModuleOutputWattR.1…n | .1.3.6.1.4.1.935.10.1.1.4.2.1.8
| upsEModuleOutputLoadR.1….n | .1.3.6.1.4.1.935.10.1.1.4.2.1.9
| upsEModuleWarningCode.1…..n | .1.3.6.1.4.1.935.10.1.1.4.2.1.10
| upsEModuleFaultCode.1….n | .1.3.6.1.4.1.935.10.1.1.4.2.1.11
| upsEModuleTrapState.1…..n | .1.3.6.1.4.1.935.10.1.1.4.2.1.12
| upsEModuleConfigOutputVA.1….n | .1.3.6.1.4.1.935.10.1.1.4.2.1.13
| upsEModuleOutputCurrentS.1….n | .1.3.6.1.4.1.935.10.1.1.4.2.1.14
| upsEModuleOutputCurrentT.1….n | .1.3.6.1.4.1.935.10.1.1.4.2.1.15
| upsEModuleOutputWattS.1…..n | .1.3.6.1.4.1.935.10.1.1.4.2.1.16
| upsEModuleOutputWattT.1….n | .1.3.6.1.4.1.935.10.1.1.4.2.1.17
| upsEModuleOutputLoadS.1….n | .1.3.6.1.4.1.935.10.1.1.4.2.1.18
| upsEModuleOutputLoadT.1….n | .1.3.6.1.4.1.935.10.1.1.4.2.1.19
| upsEModuleOutputVAR.1…..n | .1.3.6.1.4.1.935.10.1.1.4.2.1.20
| upsEModuleOutputVAS.1…n | .1.3.6.1.4.1.935.10.1.1.4.2.1.21
| upsEModuleOutputVAT.1….n | .1.3.6.1.4.1.935.10.1.1.4.2.1.22
upsELoadSegment
| upsELoadSegment1OffDelay | .1.3.6.1.4.1.935.10.1.1.5.1
| upsELoadSegment1OnDelay | .1.3.6.1.4.1.935.10.1.1.5.2
| upsELoadSegment1AutoOffTimer | .1.3.6.1.4.1.935.10.1.1.5.3
| upsELoadSegment1AutoOnTimer | .1.3.6.1.4.1.935.10.1.1.5.4
| upsELoadSegment1State | .1.3.6.1.4.1.935.10.1.1.5.5
| upsELoadSegment2OffDelay | .1.3.6.1.4.1.935.10.1.1.5.6
| upsELoadSegment2OnDelay | .1.3.6.1.4.1.935.10.1.1.5.7
| upsELoadSegment2AutoOffTimer | .1.3.6.1.4.1.935.10.1.1.5.8
| upsELoadSegment2AutoOnTimer | .1.3.6.1.4.1.935.10.1.1.5.9
| upsELoadSegment2State | .1.3.6.1.4.1.935.10.1.1.5.10
upsEEnvironment
ups Eenvironment Temperature | upsEEnvironmentCurrentTemperature.0 | .1.3.6.1.4.1.935.10.1.1.6.1.1
| upsEEnvironmentTemperatureHighSetPoint.0 | .1.3.6.1.4.1.935.10.1.1.6.1.2
| upsEEnvironmentTemperatureHighStatus.0 | .1.3.6.1.4.1.935.10.1.1.6.1.3
| upsEEnvironmentTemperatureLowSetPoint.0 | .1.3.6.1.4.1.935.10.1.1.6.1.4
| upsEEnvironmentTemperatureLowStatus.0 | .1.3.6.1.4.1.935.10.1.1.6.1.5
| upsEEnvironmentTemperatureOffset.0 | .1.3.6.1.4.1.935.10.1.1.6.1.6
ups Eenvironment Humidity | upsEEnvironmentCurrentHumidity.0 | .1.3.6.1.4.1.935.10.1.1.6.2.1
| upsEEnvironmentHumidityHighSetPoint.0 | .1.3.6.1.4.1.935.10.1.1.6.2.2
| upsEEnvironmentHumidityHighStatus.0 | .1.3.6.1.4.1.935.10.1.1.6.2.3
| upsEEnvironmentHumidityLowSetPoint.0 | .1.3.6.1.4.1.935.10.1.1.6.2.4
| upsEEnvironmentHumidityLowStatus.0 | .1.3.6.1.4.1.935.10.1.1.6.2.5
| upsEEnvironmentHumidityOffset.0 | .1.3.6.1.4.1.935.10.1.1.6.2.6
| upsEEnvironmentContactsNum.0 | .1.3.6.1.4.1.935.10.1.1.6.3
upsEEnvironmentContactTable | upsEEnvironmentContactType | .1.3.6.1.4.1.935.10.1.1.6.4.1.2
| upsEEnvironmentContactState | .1.3.6.1.4.1.935.10.1.1.6.4.1.3
| upsEEnvironmentContactDescription | .1.3.6.1.4.1.935.10.1.1.6.4.1.4
upsEBatteryTest
| upsEBatteryTestStart.0 | .1.3.6.1.4.1.935.10.1.1.7.1
| upsEBatteryTestSettingTime.0 | .1.3.6.1.4.1.935.10.1.1.7.2
| upsEBatteryTestResult.0 | .1.3.6.1.4.1.935.10.1.1.7.3
| upsEBatteryTestStartTime.0 | .1.3.6.1.4.1.935.10.1.1.7.4
| upsEBatteryTestElapsedTime.0 | .1.3.6.1.4.1.935.10.1.1.7.5
ups Ebattery TestScheduleTable | upsEBatteryTestScheduleDay.1….7 | .1.3.6.1.4.1.935.10.1.1.7.6.1.2
| upsEBatteryTestScheduleTime.1…7 | .1.3.6.1.4.1.935.10.1.1.7.6.1.3
| upsEBatteryTestScheduleType.1…7 | .1.3.6.1.4.1.935.10.1.1.7.6.1.5
| upsEBatteryTestScheduleTestWithTime.1.7 | .1.3.6.1.4.1.935.10.1.1.7.6.1.6
| upsEBatteryTestScheduleSpecialDay.1..7 | .1.3.6.1.4.1.935.10.1.1.7.6.1.7
upsEControl
| upsEControlOutputOffDelay.0 | .1.3.6.1.4.1.935.10.1.1.8.1
| upsEControlOutputOnDelay.0 | .1.3.6.1.4.1.935.10.1.1.8.2
| upsEControlOutputOnOffControl.0 | .1.3.6.1.4.1.935.10.1.1.8.3
upsEShutdownEventsTable | upsEShutdownEventAction.1…12 | .1.3.6.1.4.1.935.10.1.1.8.4.1.2
| upsEShutdownwarningPeriodTime.1…12 | .1.3.6.1.4.1.935.10.1.1.8.4.1.3
| upsEShutdownWarningPeriodInterval.1---12 | .1.3.6.1.4.1.935.10.1.1.8.4.1.4
upsEControlWeeklyScheduleTable | upsEWeeklyScheduleShutdownDay.1….7 | .1.3.6.1.4.1.935.10.1.1.8.5.1.2
| upsEWeeklyScheduleShutdownTime.1….7 | .1.3.6.1.4.1.935.10.1.1.8.5.1.3
| upsEWeeklyScheduleRestartDay.1….7 | .1.3.6.1.4.1.935.10.1.1.8.5.1.4
| upsEWeeklyScheduleRestartTime.1…7 | .1.3.6.1.4.1.935.10.1.1.8.5.1.5
upsEWeeklyScheduleRestartTime.1 | upsESpecialDayScheduleShutdownDay.1…8 | .1.3.6.1.4.1.935.10.1.1.8.6.1.2
| upsESpecialDayScheduleShutdownTime.1…8 | .1.3.6.1.4.1.935.10.1.1.8.6.1.3
| upsESpecialDayScheduleRestartDay.1…8 | .1.3.6.1.4.1.935.10.1.1.8.6.1.4
| upsESpecialDayScheduleRestartTime.1….8 | .1.3.6.1.4.1.935.10.1.1.8.6.1.5
upsETrapControl
upsETrapsReceiversTable | upsETrapsReceiverAddress.1…8 | .1.3.6.1.4.1.935.10.1.1.9.1.1.2
| upsETrapReceiverCommunityString.1…8 | .1.3.6.1.4.1.935.10.1.1.9.1.1.3
| upsETrapType.1…8 | .1.3.6.1.4.1.935.10.1.1.9.1.1.4
| upsETrapsSeverityLevel.1…8 | .1.3.6.1.4.1.935.10.1.1.9.1.1.5
| upsETrapReceiverDescription.1…8 | .1.3.6.1.4.1.935.10.1.1.9.1.1.6
| upsETrapState.0 | .1.3.6.1.4.1.935.10.1.1.9.2

## 1628 OID
upsIdent
| upsIdentManufacturer.0 | .1.3.6.1.2.1.33.1.1.1
| upsIdentModel.0 | .1.3.6.1.2.1.33.1.1.2
| upsIdentUPSSoftwareVersion.0 | .1.3.6.1.2.1.33.1.1.3
| upsIdentAgentSoftwareVersion.0 | .1.3.6.1.2.1.33.1.1.4
| upsIdentName.0 | .1.3.6.1.2.1.33.1.1.5
| upsIdentAttachedDevices.0 | .1.3.6.1.2.1.33.1.1.6
upsBattery
| upsBatteryStatus.0 | .1.3.6.1.2.1.33.1.2.1
| upsSecondsOnBattery.0 | .1.3.6.1.2.1.33.1.2.2
| upsEstimatedMinutesRemaining.0 | .1.3.6.1.2.1.33.1.2.3
| upsEstimatedChargeRemaining.0 | .1.3.6.1.2.1.33.1.2.4
| upsBatteryVoltage.0 | .1.3.6.1.2.1.33.1.2.5
| upsBatterymandatory.0 | .1.3.6.1.2.1.33.1.2.6
| upsBatteryTemperature.0 | .1.3.6.1.2.1.33.1.2.7
upsInput
| upsInputLineBads.0 | .1.3.6.1.2.1.33.1.3.1
| upsInputNumLines.0 | .1.3.6.1.2.1.33.1.3.2
upsInputTable | upsInputFrequency.1 | .1.3.6.1.2.1.33.1.3.3.1.2
upsInputFrequency.2
upsInputFrequency.3
| upsInputVoltage.1 | .1.3.6.1.2.1.33.1.3.3.1.3
upsInputVoltage.2
upsInputVoltage.3
| upsInputmandatory.1 | .1.3.6.1.2.1.33.1.3.3.1.4
upsInputmandatory.2
upsInputmandatory.3
| upsInputTruePower.1 | .1.3.6.1.2.1.33.1.3.3.1.5
upsInputTruePower.2
upsInputTruePower.3
upsOutput
| upsOutputSource.0 | .1.3.6.1.2.1.33.1.4.1
| upsOutputFrequency.0 | .1.3.6.1.2.1.33.1.4.2
| upsOutputNumLines.0 | .1.3.6.1.2.1.33.1.4.3
upsOutputTable | upsOutputVoltage.1 | .1.3.6.1.2.1.33.1.4.4.1.2
upsOutputVoltage.2
upsOutputVoltage.3
| upsOutputmandatory.1 | .1.3.6.1.2.1.33.1.4.4.1.3
upsOutputmandatory.2
upsOutputmandatory.3
| upsOutputPower.1 | .1.3.6.1.2.1.33.1.4.4.1.4
upsOutputPower.2
upsOutputPower.3
| upsOutputPercentLoad.1 | .1.3.6.1.2.1.33.1.4.4.1.5
upsOutputPercentLoad.2
upsOutputPercentLoad.3
upsBypass
| upsBypassFrequency.0 | .1.3.6.1.2.1.33.1.5.1
| upsBypassNumLines.0 | .1.3.6.1.2.1.33.1.5.2
upsBypassTable | upsBypassVoltage.1 | .1.3.6.1.2.1.33.1.5.3.1.2
upsBypassVoltage.2
upsBypassVoltage.3
| upsBypassmandatory.1 | .1.3.6.1.2.1.33.1.5.3.1.3
upsBypassmandatory.2
upsBypassmandatory.3
| upsBypassPower.1 | .1.3.6.1.2.1.33.1.5.3.1.4
upsBypassPower.2
upsBypassPower.3
upsAlarm
| upsAlarmsPresent.0 | .1.3.6.1.2.1.33.1.6.1
| upsAlarmId | .1.3.6.1.2.1.33.1.6.2.1.1
| upsAlarmDescr | .1.3.6.1.2.1.33.1.6.2.1.2
upsTest
| upsTestId.0 | .1.3.6.1.2.1.33.1.7.1
| upsTestSpinLock.0 | .1.3.6.1.2.1.33.1.7.2
| upsTestResultsSummary.0 | .1.3.6.1.2.1.33.1.7.3
| upsTestResultsDetail.0 | .1.3.6.1.2.1.33.1.7.4
| upsTestStartTime.0 | .1.3.6.1.2.1.33.1.7.5
| upsTestElapsedTime.0 | .1.3.6.1.2.1.33.1.7.6
upsWellKnownTests |  | .1.3.6.1.2.1.33.1.7.7
upsControl
| upsShutdownType.0 | .1.3.6.1.2.1.33.1.8.1
| upsShutdownAfterDelay.0 | .1.3.6.1.2.1.33.1.8.2
| upsStartupAfterDelay.0 | .1.3.6.1.2.1.33.1.8.3
| upsRebootWithDuration.0 | .1.3.6.1.2.1.33.1.8.4
| upsAutoRestart.0 | .1.3.6.1.2.1.33.1.8.5
upsConfig
| upsConfigInputVoltage.0 | .1.3.6.1.2.1.33.1.9.1
| upsConfigInputFreq.0 | .1.3.6.1.2.1.33.1.9.2
| upsConfigOutputVoltage.0 | .1.3.6.1.2.1.33.1.9.3
| upsConfigOutputFreq.0 | .1.3.6.1.2.1.33.1.9.4
| upsConfigOutputVA.0 | .1.3.6.1.2.1.33.1.9.5
| upsConfigOutputPower.0 | .1.3.6.1.2.1.33.1.9.6
| upsConfigLowBattTime.0 | .1.3.6.1.2.1.33.1.9.7
| upsConfigAudibleStatus.0 | .1.3.6.1.2.1.33.1.9.8
| upsConfigLowVoltageTransferPoint.0 | .1.3.6.1.2.1.33.1.9.9
| upsConfigHighVoltageTransferPoint.0 | .1.3.6.1.2.1.33.1.9.10